[image: image1.jpg]SAINT
PAUL






November 15, 2010

RED BRANCH CORP

1300 INGERSON ROAD

ARDEN HILLS MN  55112-3762

NOTICE OF CONDEMNATION

UNFIT FOR HUMAN HABITATION

ORDER TO VACATE

RE:
513 VAN BUREN AVE   

Dear Property Representative:

Your building was inspected on November 15, 2010.

The building was found to be unsafe, unfit for human habitation, a public nuisance, a hazard to the public welfare or otherwise dangerous to human life. A Condemnation Placard has been posted on the building.

The following deficiency list must be completed or the building vacated by the re-inspection date.

CONDEMNATION OF THE BUILDING REVOKES THE CERTIFICATE OF OCCUPANCY.

Failure to complete the corrections may result in a criminal citation. The Saint Paul Legislative Code requires that no building be occupied without a Fire Certificate of Occupancy.

DEFICIENCY LIST

1.
Exterior - SPLC 34.09 (3), 34.32 (3) - Repair and maintain the door in good condition.-Repair the rear door that does not work.

2.
Exterior - SPLC 34.09 (3), 34.32 (3) - Repair and maintain the window frame. 

3.
Exterior - SPLC 34.09 (3), 34.32 (3) - Repair and maintain the window glass. 

4.
Exterior - SPLC 34.09 (3), 34.32 (3) - Provide or repair and maintain the window screen. 

5.
Interior - MN Rules 1300.0180 - Immediately discontinue use of unsafe heating appliance until repaired or replaced by a licensed contractor.  This work may require a permit(s).  Call DSI at (651) 266-9090.  Red tags may not be removed except by fire department inspector. 

6.
Interior - SPLC 34.11 (6), 34.34 (3) - Provide service of heating facility by a licensed contractor which must include a carbon monoxide test.  Submit a completed copy of the Saint Paul Fire Marshal's Existing Fuel Burning Equipment Safety Test Report to this office. 

7.
Interior - UMC 504.6 - Provide, repair or replace the dryer exhaust duct.  Exhaust ducts for domestic clothes dryers shall be constructed of metal and shall have a smooth interior finish.  The exhaust duct shall be a minimum nominal size of four inches (102 mm) in diameter.  This work may require a permit(s).  Call DSI at (651) 266-8989. 

8.
Interior - SPLC 34.11 (5), 34.34 (2) - Contact a licensed contractor to repair or replace the water heater.  This work may require a permit(s).  Call DSI at (651) 266-9090. 

9.
Interior - SPLC 34.11 (6) - Provide and maintain a minimum of 68 degrees F in all habitable rooms at all times. 

10.
Interior - SPLC 34.10 (6), 34.33 (5) - Exterminate and control insects, rodents or other pests.  Provide documentation of extermination.-Hire a licensed exterminator to eliminate mice.

11.
Interior - MFGC 409.5 - Provide an approved gas shut off valve within 6 feet of the appliance in accordance with the mechanical code.  This work may require a permit(s).  Call DSI at (651) 266-8989. 

12.
Interior - SPLC 34.13 (3), SPLC 34.17 (2) - Reduce and maintain the number of occupants in the sleeping rooms. 

13.
Interior - SPLC 34.13 (2), (3), SPLC 34.17 (2) - Reduce and maintain the number of occupants in the unit. 

14.
Interior - MN State Statute 299F.50 Immediately provide and maintain an approved Carbon Monoxide Alarm in a location within ten (10) feet of each sleeping area.  Installation shall be in accordance with manufacturers instructions. 

15.
Interior - SPLC 34.09 (3) i - Repair and maintain an approved one-inch throw single cylinder deadbolt lock.-Remove the illegal deadbolt on the front door.

16.
Interior - MSFC 1003.3.1.8 - Remove unapproved locks from the unit doors.  The door must be openable from the inside without the use of keys or special knowledge or effort. 

17.
Interior - MN Stat. 299F.362 - Immediately provide and maintain a smoke detector located outside each sleeping area. 

18.
Interior - MSFC 605.1- All light fixtures shall be maintained with protective globes if originally equipped. 

19.
Interior - MSFC 315.2 - Provide and maintain orderly storage of materials. 

20.
Interior - MSFC 2705.4.1 - Remove and maintain the hazardous materials storage.-Immediately remove the lawn mower from the home.

21.
Interior - SPLC 200.02 (a) No person shall own, harbor, keep or maintain in the City and dog over three months of age without a license.  Provide written documentation of current license to the Fire Inspector.  To obtain a dog license, contact DSI at 651-266-8989 

22.
Interior - SPLC 34.10 (3), 34.33(2) - Provide an approved handrail. The top of the handrail must be between 34 and 38 inches above the treads and run the entire length of the stair. 

23.
Interior - MSFC 605.6 - Provide electrical cover plates to all outlets, switches and junction boxes where missing.-Hire a licensed electrician to repair damaged outlets including the kitchen outlet near the stove.

24.
Interior - SPLC 34.10 (7), 34.33 (6) - Repair and maintain the walls in an approved manner. 

25.
Interior - SPLC 34.23, MSFC 110.1 - This occupancy is condemned as unfit for human habitation.  This occupancy must not be used until re-inspected and approved by this office.-This building is condemned for lack of basic facility.  No heat.

26.
SPLC 34.11 (6), 34.34 (3) - Provide service of heating facility by a licensed contractor which must include a carbon monoxide test.  Submit a completed copy of the Saint Paul Fire Marshal's Existing Fuel Burning Equipment Safety Test Report to this office. 

27.
SPLC 39.02(c) - Complete and sign the provided smoke detector affidavit and return it to this office. 

For an explanation or information on some of the violations contained in this report, please visit our web page at:  http://www.ci.stpaul.mn.us/index.aspx?NID=211

You have the right to appeal these orders to the Legislative Hearing Officer. Applications for appeals may be obtained at the Office of the City Clerk, 310 City Hall, City/County Courthouse, 15 W Kellogg Blvd, Saint Paul MN  55102  Phone:  (651-266-8688) and must be filed within 10 days of the date of the original orders.

If you have any questions, email me at:  lisa.martin@ci.stpaul.mn.us or call me at 

651-266-8988 between 6:30 - 8:30 a.m.  Please help make Saint Paul a safer place in which to live and work.

Sincerely,

Lisa Martin
Fire Inspector

Housing Resource Center

Force Unit
An Equal Opportunity Employer

